# ISAT GUIDE SPECIFICATION (CBC 2007, OSHPD)

# SECTION  [________]

# SEISMIC RESTRAINT OF SUSPENDED UTILITIES

  - DESCRIPTION

    - Provide engineered seismic restraint systems for suspended [Electrical] [Electrical Equipment] [Plumbing] [Mechanical Piping] [Process Piping] [HVAC Duct] [Mechanical Equipment] utilities compliant with the currently adopted version of the California Building Code (CBC) with OSHPD amendments.

    - At seismic restraint installation locations, provide vertical support systems engineered to accommodate dead load plus seismic force reactions.

  - RELATED SPECIFICATION SECTIONS

[Electrical]

[Electrical Equipment]

[Plumbing]

[Mechanical Piping]

[Process Piping]

[HVAC Duct]

[Mechanical Equipment]

  - REFERENCES

    - Publications, codes and standards listed below form a part of this specification to the extent referenced.

      - Applications, Design and Inspection Manual  -Engineered Seismic Bracing of Suspended Utilities-  2007 California Building Code Edition,  OPA-0485-07

International Seismic Application Technology (ISAT)

[Vol. 1 – Distributed Electrical Systems & Equipment]

[Vol. 2 – HVAC Duct, Mechanical Piping, Plumbing, Process Piping & 			   Equipment]

      - 2007 California Building Code (CBC) - Title 24, Part 2, Volume 2,

Chapter 16A

      - ASCE 7-05, Chapter 13, Minimum Design Loads For Buildings and Other Structures, American Society of Civil Engineers (ASCE)

      - ACI 318-05, Building Code Requirements for Structural Concrete,

American Concrete Institute (ACI).

  - COMPONENT IMPORTANCE FACTOR

    - Per OSHPD, Importance Factor for all components shall be IP = 1.5.

    - Consult the ISAT Applications, Design and Inspection Manual or contact ISAT for a summary of components not required to be restrained by code.

  - SUBMITTALS

    - Contractor to identify and convey to ISAT each overhead deck condition to which seismic attachments will be made.  Information to include type and density of concrete, concrete thickness, size and gage of metal deck, type and size of steel member and any point load limitations or restrictions.

    - Provide Seismic Design Force calculations per ASCE 7- 05, Formulas 13.3-1 thru 13.3-3 stamped by a [registered design professional][qualified civil or structural engineer] licensed to practice in the State of California.  For multi-story projects, provide calculated Seismic Design Force for each floor.

    - If not already furnished in contract documents, submit seismic restraint layouts stamped by a [registered design professional][qualified civil or structural engineer] licensed to practice in the State of California.  Seismic restraint layouts to show:

- All vertical support and seismic brace locations.

- All anchorage connections to structure. Anchor brand, type, quantity and size.

- Vertical support and brace reaction point load at all connections to structure.   For review by engineer of record in checking suitability of the building structure to accommodate imposed loads.

- Plan set sheets showing appropriate installation details reflecting actual job site conditions.

    - Include cover sheet with Seismic Restraint Bracing Legend delineating:

- Maximum Allowable Size or Utility Weight (Lbs/Lf).

- Minimum Vertical Support Rod Diameter.

- Support Rod Total Vertical Load.

- Maximum Allowable Transverse Brace Spacing.

- Transverse Brace Reaction.

- Maximum Allowable Longitudinal Brace Spacing.

- Longitudinal Brace Reaction.

- Minimum Required Seismic Restraint Brace Arm Assembly.

- Minimum Required Seismic Restraint Anchorage To Overhead Structure.

- Installation Detail Drawing References

PART 2 - PRODUCTS

2.1	ACCEPTABLE MANUFACTURERS

    - Seismic restraint hardware and engineering to be that furnished by International Seismic Application Technology (ISAT)  877-999-4728,  www.isatsb.com.

    - Vertical support and seismic restraint anchorages are to utilize ISAT Blue Banger Hanger Cast-In Place Deck Inserts unless noted otherwise.  Post installed anchors are an acceptable alternate provided the anchors are those pre-engineered within the ISAT Applications, Design and Inspection Manual.

    - Vertical support and seismic restraint connections to structural steel are to utilize ISAT BC-4 Beam Clamp connections unless noted otherwise.  Welded or bolted connections are an acceptable alternate provided the details employed are those pre-engineered within the ISAT Applications, Design and Inspection Manual.

PART 3 - EXECUTION

3.1	INSTALLATION

    - Vertical support and seismic restraint anchorages to be per the ISAT Applications, Design and Inspection Manual, 2007 CBC Edition.

    - For conditions not covered within the ISAT Applications, Design and Inspection Manual, the required engineering is to be performed by ISAT.

    - ISAT shall provide field installation training prior to commencement of install.

    - Field relocation of any seismic installation points away from that shown on the ISAT furnished shop drawing layouts shall be coordinated with ISAT Technical Service.

    - Consult ISAT Technical Service when field conditions prohibit compliance with the supplied installation details.

    - In order to satisfy ASCE 7 minimum yield strength requirements, the allowable brace spacing for non-ductile systems (eg. cast iron, plastic and glass pipe) shall be no more than half that for ductile systems.

3.2	EQUIPMENT CONNECTIONS

A.	Where seismic bracing is allowed to be omitted due to component size or proximity to overhead deck, all terminations to fixed equipment, panels, etc. or to other portions of the system requiring seismic restraint are to utilize flexible connectors.

Where seismic bracing is allowed by code to be omitted due to size or proximity to overhead deck, the inspector of record or others, shall be responsible for assuring that damaging impact or vertical support failure cannot occur. Assessment as to conformance with this requirement is outside ISAT’s scope of responsibility.